## Sheet1
Orifice plate calculation Calculation of minimum plate thickness for restriction orifice. |  | Input field
|  |  | mm | Inch |  | Absolut min | Bidirektional | Ok
Line size ID | mm | 25
DP Differentialpressure | Mpa | 0.1
Yield stress of plate | Mpa | 220
β Ratio | - | 0.7
Calculated min. thickness (Miller) to sustain stress |  |  | 0.25299 | 0.0099604
Calculated min thickness ( e@bore) ISO 5167 |  |  | 0.125 | 0.0049213
Min thickness ISO & (Miller) |  |  | 0.25299 | 0.0099604 |  | 0.5 | 1 |  | Bidirectional orifice without bevel - thickness: 0.25 to 0.5 mm.
Calculated max thickness ( e@bore) ISO 5167 |  |  | 0.5 | 0.019685 |  |  |  | 1 | Unidirectional orifice with bevel 0.5 to 1.25 mm.
Calculated max thickness plate ISO5157 |  |  | 1.25
Bidirectional orifice without bevel - thickness: 0.25 to 0.5 mm.
Unidirectional orifice with bevel 0.5 to 1.25 mm.
Stainless steel
SS-EN 10088 |  | Yield stress1 | Breaking limit2 | SIS | AISI
Austenitiska | 1.4301 | 210 MPa | 650 MPa | SS-2333 | 304
| 1.4436 | 220 MPa | 650 MPa | SS-2343 | 316
Duplexa | 1.4362 | 400 MPa | 700 MPa | SS-2327 | S32304
| 1.4462 | 460 MPa | 800 MPa | SS-2377 | S32205
1) Yield stress for stainless steel is normally defined as 022 % remaining stress.
2) Approximate value.
Thickness in mm.>sqrt((0.681-0.651*β)*DP/Yeldstress)*ID
Conforms to Miller
ISO 5167
The thickness e of the orifice shall be between 0,005D and 0,02D.